## Slide 1: Winding Design in Hydro Generators
M. Samet yakut – 14.03.2023

## Slide 2: Content
Winding Types
Wave Winding Design
Roebel Transposition
Conclusion
Past Plans
Future Plans
References

## Slide 3: Winding Types

## Slide 4: Winding Types
Wave Winding |  | Lap Winding | 
Advantage | Disadvantage | Advantage | Disadvantage
Less outage duration | Complicated design | Simple winding schematic design | Complicated end connections
Simple end connection | Generally requires more coil types | Less type of coils | More outage time
Low number of external connection | Longer average winding pitches, therefore longer end windings | Allows bypass | Sophisticated production

## Slide 5: Winding Types

## Slide 6: Wave Winding Design
Integer/Fractional Slot
In our case: Q = 300, p = 32, m = 3

## Slide 7: Wave Winding Design
Alternatively:

## Slide 8: Wave Winding Design
Selection of coil pitch (Y):
  Winding factor (> 0.95)
  If possible, eliminating dominant harmonics or reducing
  Y = 9 is suitable for 300 slots 32 poles

## Slide 9: Wave Winding Design
Problem: Constant throw of Y = 9 is not possible!
Solution: , and are integers
, and =10
Result:
Design the top windings and shift bottoms by Y number of slots
    Alternatively: Zone Short-Pitching

## Slide 10: Wave Winding Design

## Slide 11: Wave Winding Design

## Slide 12: Roebel Transposition

## Slide 13: Roebel Transposition
Aim: Reducing AC losses
Method: Spirs and transposition
180º, 360º, 540º or 720º
360º is common in hydro generators

## Slide 14: Roebel Transposition

## Slide 15: Roebel Transposition

## Slide 16: Roebel Transposition

## Slide 17: Roebel Transposition

## Slide 18: Conclusion
Electromagnetically, there is no difference between wave and lap windings.
Again, there is no difference between zone-short pitching and conventionally short pitching.
360º Roebel transposition is generally suitable for hydro generators, as well as our case.

## Slide 19: Past Plans
Conference paper published: WEMDCD23 / Winding Type Alternation of a Refurbished Old Generator

## Slide 20: Future Plans
Completing winding design
Calibration of analytical model with Maxwell 3D
Journal article until end of June

## Slide 21: References
[1] G. Traxler-Samek and M. Lecker, "Three-Phase Winding Design for Large Hydro-Generators," 2020 International Conference on Electrical Machines (ICEM), Gothenburg, Sweden, 2020, pp. 2657-2663, doi: 10.1109/ICEM49940.2020.9271049.
[2] Pyrhonen, Juha, Tapani Jokinen and Valéria Hrabovcová. “Design of Rotating Electrical Machines.” (2009).