## Slide 2
REFURBISHMENT & ALTERNATING WINDING TYPE OF A 44 MVA HYDRO GENERATOR
M. Samet YAKUT
Advisor: Assoc. Prof. Ozan Keysan
November 23, 2023
EE590 Seminar, METU EE Dep.

## Slide 3
Largest low-carbon electricity generation technology is hydropower [1]
IEA, Low-carbon electricity generation by technology, 2020, IEA, Paris https://www.iea.org/data-and-statistics/charts/low-carbon-electricity-generation-by-technology-2020, IEA. Licence: CC BY 4.0
TWh
Notes: The importance of the hydro generators arises from the fact that the largest low carbon electricity source is the hydro power according to a research conducted in 2020 by International Energy Agency. The installed capacity of the hydro power is more than 4000 TWh which is higher than the total installed capacity of the other renewable energy resources.

## Slide 4: Outline
Introduction
  Basic Terms & Definitions
Refurbishment Process
  Optimization
  Design of Windings
Conclusion

## Slide 5: Hydro Generators
Largest low carbon energy resource
Salient pole synchronous machines
High voltage stator
Tens of kVA to hundreds of MVA
IEA, Low-carbon electricity generation by technology, 2020, IEA, Paris https://www.iea.org/data-and-statistics/charts/low-carbon-electricity-generation-by-technology-2020, IEA. Licence: CC BY 4.0

## Slide 6: Refurbishment
Installed capacity older than 30 years: 6205 MWs
  which accounts for 31.9% of large hydro generators
Most old generators are over – designed
  cheapest way of increasing installed power
N. Tosun, G. Gülletutan, M. S. Yakut, D. Alp Yilmaz, Ö. Bayer and O. Keysan, "Winding Type Alternation of a Refurbished Old Generator," 2023 IEEE Workshop on Electrical Machines Design, Control and Diagnosis (WEMDCD), Newcastle upon Tyne, United Kingdom, 2023, pp. 1-6, doi: 10.1109/WEMDCD55819.2023.10110941.

## Slide 7: Winding Types
Lap Winding Wave Winding
M.M. Znidarich (2008) Hydro Generator High Voltage Stator Windings: Part 1 – Essential Characteristics and Degradation Mechanisms, Australian Journal of Electrical and Electronics Engineering, 5:1, 1-17, DOI: 10.1080/1448837X.2008.11464196

## Slide 8: Winding Types
Wave Winding
  Less outage duration
  Simple end connection
  Low number of external connections
Lap Winding
  Simple winding schematic design
  Less type of coils
  Allows bypass

## Slide 9: Problem Definition
Refurbishment of an old 44 MVA hydro generator by changing winding type from lap to wave
Constraints
  Constant outer diameter
  Same rotor geometry

## Slide 10: Optimization: Method
NSGA – II
Variables are machine geometry parameters
Simulations in RMxprt

## Slide 11: Optimization: Objective Function
Objective functions are
  Initial cost
  Efficiency
Subject to

## Slide 12: Optimization: Penalty Function
SCR should not be less than 0.8
Hence
  where A is a very large number compared to initial cost
Glenn Mottershead; Stefano Bomben; Isidor Kerszenbaum; Geoff Klempner, "OPERATION AND CONTROL," in Handbook of Large Hydro Generators: Operation and Maintenance , IEEE, 2021, pp.177-240, doi: 10.1002/9781119524205.ch4.

## Slide 13: Optimization: Results
Notes: As previously mentioned, the algorithm is run for different outer diameters and results are shown here. 6858 mm is the nominal outer diameter. The results show that if there is not 98% efficiency constraint, there is no need to increase the outer diameter. The same efficiency can be reached with nominal diameter with less cost. However, to reach a certain efficiency levels such that 98.1 98.2%, we need to increase the outer diameter to reach that values. The remaining part is to design the windings to reduce the AC losses. For that purpose, we are utilizing Roebel transposition.

## Slide 14: Roebel Bars
Different induced voltages in each strand
Circulating currents
Eddy losses

## Slide 15: Roebel Bars
Transposition is applied to minimize circulating currents
Common transposition angles: 180, 360, 540 and 720
Transposed in active region
Notes: Roebel bars are composed of a number of strands, and they are single turn coils. The transposition is applied to minimize eddy and circulating currents. The transposition is defined with an angle such that if the transposition is 360 degree, the strands are transposed in a way that figure shows. There are 180, 540 and 720 degree transpositions as well but 360 degree is the common practice in hydro generators. The larger values are used in turbo generators.

## Slide 16: Design of Roebel Bars
Strand number is swept
Strand dimensions are calculated by including manufacturing details
AC and DC resistances are also calculated

## Slide 17: Design of Roebel Bars

## Slide 18: Design of Roebel Bars

## Slide 19: Design of Roebel Bars

## Slide 20: Conclusion & Future Work
Refurbishment is important for sustanability
  Cheapest way of increasing installed power
Roebel bars are used to cancel circulating currents
Future Work: Optimization with different rotor geometries
      Production and test of different insulation materials